[image: image1.jpg]



                     BTS West
Cust Code
BioSolar Group / CytoCulture
1711 Orbit Way -- Bldg 2
Attention Of
Randall von Wedel, Ph.D.  RvWedel@gmail.com
Minden, NV 89423
Company
CytoCulture International, Inc.

TEL:   775-783-4660
End User






 City of San Francisco
FAX:   775-783-4651

Taken
1/30/2008
Received
1/31/2008
Unit ID
08-12  Rail Car  Prox77244
Tested
1/31/2008
Reported
1/31/2008
Test Pkg
FTG+TAN+KFW+FPCC

Fuel Type
Biodiesel Fuel

   Biodiesel Quality Status Report for B100: Rail Car Prox77244 sampled on 01/30/2008
Unit ID
08-12
Batch Number
7055

Date Sampled
1/30/2008
Sample Number
3332

Test Name
Test Method
Limit
Result
Status

Free Glycerin (mass %)
ASTM D 6584
MAX 0.020
0.000
PASS

Monoglycerides (mass %)
ASTM D 6584
N/A
0.000
N/A

Diglycerides (mass %)
ASTM D 6584
N/A
0.019
N/A

Triglycerides (mass %)
ASTM D 6584
N/A
0.000
N/A

Total Glycerin (mass %)
ASTM D 6584
MAX 0.240
0.019
PASS

Flash Point, Closed Cup (°C)
ASTM D 93
MIN 130
184
PASS

KF Water (ppm)
ASTM D 6304
N/A
725
N/A

TAN (mg KOH/g)
ASTM D 664
MAX 0.50
0.13
PASS









B100 fuel (top/middle/bottom) vs. corresponding pHLip Test Result (B100 Reference on right) at 10 min.
                                   [image: image2.jpg]



Rail Car Prox 77244 B100 sampled on January 30, 2008 and corresponding pHLip Test Results on the same day for Top, Middle and Bottom of the rail car.  pHLip Test results indicate excellent quality biodiesel with no color change or turbidity in the red indicator solution, clear and bright B100 fuel layer and a perfect mirror finish in all 3 test vials. There is no evidence of any contaminants as corroborated by the laboratory analytical data for the composite sample (25% top:50% middle:25% bottom). The composite sample passed all 4 of the selected tests for ASTM D-6751.  The total free & bound glycerin level was very low at only 0.019% (monoglycerides were below detection). KF moisture was 3x higher than normal suggesting the biodiesel may have been exposed to rain/weather in transit or upon arrival in CA. However, the low acid number (TAN = 0.13) indicates the fuel had not oxidized appreciably. The moisture in the fuel should not present a problem for high turn-over fueling applications  but it is worth discussing with supplier & distributor.  Conclusion: Excellent, clean biodiesel although somewhat moist.

