BTS West	Cust Code	BioSolar Group / CytoCulture

1711 Orbit Way -- Bldg 2	Attention Of	Randall von Wedel, Ph.D.  RvWedel@gmail.com

Minden, NV 89423	Company	CytoCulture International, Inc.

TEL:   775-783-4660	End User							 City of San Francisco

FAX:   775-783-4651

Taken	1/30/2008	Received	1/31/2008	Unit ID	08-12  Rail Car  Prox77244

Tested	1/31/2008	Reported	1/31/2008	Test Pkg	FTG+TAN+KFW+FPCC

Fuel Type	Biodiesel Fuel

Biodiesel Quality Status Report for B100: Rail Car Prox77244 sampled on 01/30/2008

Unit ID	08-12	Batch Number	7055

Date Sampled	1/30/2008	Sample Number	3332

Test Name	Test Method	Limit	Result	Status

Free Glycerin (mass %)	ASTM D 6584	MAX 0.020	0.000	PASS

Monoglycerides (mass %)	ASTM D 6584	N/A	0.000	N/A

Diglycerides (mass %)	ASTM D 6584	N/A	0.019	N/A

Triglycerides (mass %)	ASTM D 6584	N/A	0.000	N/A

Total Glycerin (mass %)	ASTM D 6584	MAX 0.240	0.019	PASS

Flash Point, Closed Cup (°C)	ASTM D 93	MIN 130	184	PASS

KF Water (ppm)	ASTM D 6304	N/A	725	N/A

TAN (mg KOH/g)	ASTM D 664	MAX 0.50	0.13	PASS

B100 fuel (top/middle/bottom) vs. corresponding pHLip Test Result (B100 Reference on right) at 10 min.

Rail Car Prox 77244 B100 sampled on January 30, 2008 and corresponding pHLip Test Results on the same day for Top, Middle and Bottom of the rail car.  pHLip Test results indicate excellent quality biodiesel with no color change or turbidity in the red indicator solution, clear and bright B100 fuel layer and a perfect mirror finish in all 3 test vials. There is no evidence of any contaminants as corroborated by the laboratory analytical data for the composite sample (25% top:50% middle:25% bottom). The composite sample passed all 4 of the selected tests for ASTM D-6751.  The total free & bound glycerin level was very low at only 0.019% (monoglycerides were below detection). KF moisture was 3x higher than normal suggesting the biodiesel may have been exposed to rain/weather in transit or upon arrival in CA. However, the low acid number (TAN = 0.13) indicates the fuel had not oxidized appreciably. The moisture in the fuel should not present a problem for high turn-over fueling applications  but it is worth discussing with supplier & distributor.  Conclusion: Excellent, clean biodiesel although somewhat moist.